## Sheet1
Project Name: 418 MLD WASTE WATER TREATMENT FACILITIES AT DHARAVI.
Pile Dial (mm): | 600 |  | Location : | Gas Building Test Pile-Static Load Test
Maximum Test Load (MT): | 318 |  | Effective Area of Jack: |  | 2001.9
Design Load(MT): | 127.2 |  | Dial Gauge Least Count: |  | 0.01 mm
Test Start Date: | 2026-04-09 |  | Total Settelement: |  | 8.32 mm
End Date: | 2026-06-09 |  | Net Settelement: |  | 7.04 mm
Sr.No. | Reading Interval ( Min) | Pressure Gauge Reading (Kg/cm2) | Load(MT) | Dial Gauge Reading (mm) |  |  |  | Cummulative Dial Reading | Average Dial Reading (mm) | Cumulative average Reading (mm)
|  |  |  | A | B | C | D
LOADING ( 04-09-2026)
1 | 0 | 15 | 30.0285 | 0 | 0 | 0 | 0 | 0 | 0.5375 | 0.5375 | Applied Load on Plate (MT) | Uplift (mm)
| 15 |  |  | 0.5 | 0.72 | 0.4 | 0.23 | 1.85
| 30 |  |  | 0.53 | 0.73 | 0.42 | 0.25 | 1.93
| 30 |  |  | 0.56 | 0.75 | 0.45 | 0.28 | 2.04
| 60 |  |  | 0.59 | 0.79 | 0.47 | 0.3 | 2.15
2 | 0 | 30 | 60.057 | 0.59 | 0.79 | 0.47 | 0.3 | 2.15 | 0.4975 | 1.035 | 0 | 0
| 15 |  |  | 1.01 | 1.12 | 0.91 | 0.82 | 3.86
| 30 |  |  | 1.04 | 1.16 | 0.95 | 0.86 | 4.01
| 30 |  |  | 1.06 | 1.18 | 0.97 | 0.88 | 4.09 |  |  | 30.0285 | 0.5375
| 60 |  |  | 1.08 | 1.19 | 0.98 | 0.89 | 4.14 |  |  | 60.057 | 1.035
3 | 0 | 45 | 90.0855 | 1.08 | 1.19 | 0.98 | 0.89 | 4.14 | 0.7225 | 1.7575 | 90.0855 | 1.7575
| 15 |  |  | 1.78 | 1.82 | 1.6 | 1.52 | 6.72
| 30 |  |  | 1.83 | 1.87 | 1.65 | 1.54 | 6.89
| 30 |  |  | 1.86 | 1.9 | 1.67 | 1.56 | 6.99 |  |  | 120.114 | 2.23
| 60 |  |  | 1.87 | 1.91 | 1.68 | 1.57 | 7.03 |  |  | 150.1425 | 2.8175
4 | 0 | 60 | 120.114 | 1.87 | 1.91 | 1.68 | 1.57 | 7.03 | 0.4725 | 2.23 | 180.171 | 3.4725
| 15 |  |  | 2.2 | 2.32 | 2.05 | 1.97 | 8.54
| 30 |  |  | 2.25 | 2.37 | 2.09 | 2.01 | 8.72
| 30 |  |  | 2.28 | 2.41 | 2.12 | 2.04 | 8.85 |  |  | 210.1995 | 4.7375
| 60 |  |  | 2.29 | 2.43 | 2.15 | 2.05 | 8.92 |  |  | 240.228 | 5.4175
5 | 0 | 75 | 150.1425 | 2.29 | 2.43 | 2.15 | 2.05 | 8.92 | 0.5875 | 2.8175 | 270.2565 | 6.2325
| 15 |  |  | 2.83 | 2.92 | 2.72 | 2.62 | 11.09
| 30 |  |  | 2.86 | 2.93 | 2.73 | 2.63 | 11.15
| 30 |  |  | 2.89 | 2.95 | 2.74 | 2.65 | 11.23 |  |  | 300.285 | 7.1325
| 60 |  |  | 2.9 | 2.96 | 2.75 | 2.66 | 11.27 |  |  | 320.304 | 8.1475
6 | 0 | 90 | 180.171 | 2.9 | 2.96 | 2.75 | 2.66 | 11.27 | 0.655 | 3.4725 | 320.304 | 8.3225
| 15 |  |  | 3.45 | 3.65 | 3.39 | 3.27 | 13.76 |  |  | 300.285 | 8.295
| 30 |  |  | 3.45 | 3.67 | 3.41 | 3.27 | 13.8 |  |  | 270.2565 | 8.2675
| 30 |  |  | 3.48 | 3.66 | 3.41 | 3.29 | 13.84 |  |  | 240.228 | 8.245
| 60 |  |  | 3.49 | 3.66 | 3.43 | 3.31 | 13.89 |  |  | 210.1995 | 8.2225
7 | 0 | 105 | 210.1995 | 3.49 | 3.66 | 3.43 | 3.31 | 13.89 | 1.265 | 4.7375 | 180.171 | 8.17
| 15 |  |  | 4.7 | 4.89 | 4.6 | 4.45 | 18.64 |  |  | 150.1425 | 8.1075
| 30 |  |  | 4.75 | 4.93 | 4.63 | 4.48 | 18.79 |  |  | 120.114 | 8.0225
| 30 |  |  | 4.78 | 4.95 | 4.65 | 4.5 | 18.88 |  |  | 90.0855 | 7.9
| 60 |  |  | 4.8 | 4.97 | 4.66 | 4.52 | 18.95 |  |  | 60.057 | 7.72
8 | 0 | 120 | 240.228 | 4.8 | 4.97 | 4.66 | 4.52 | 18.95 | 0.68 | 5.4175 | 30.0285 | 7.6175
| 15 |  |  | 5.62 | 5.75 | 5.15 | 5.02 | 21.54 |  |  | 0 | 7.04
| 30 |  |  | 5.63 | 5.76 | 5.16 | 5.02 | 21.57 |  |  | 15 | 7.6175
| 30 |  |  | 5.64 | 5.77 | 5.17 | 5.04 | 21.62 |  |  | 0 | 7.04
| 60 |  |  | 5.66 | 5.78 | 5.18 | 5.05 | 21.67 |  |  | 0 | 10.43
9 | 0 | 135 | 270.2565 | 5.66 | 5.78 | 5.18 | 5.05 | 21.67 | 0.815 | 6.2325 | 0 | 9.8825
| 15 |  |  | 6.35 | 6.49 | 6.02 | 5.91 | 24.77 |  |  | 0
| 30 |  |  | 6.38 | 6.53 | 6.03 | 5.93 | 24.87
| 30 |  |  | 6.39 | 6.54 | 6.03 | 5.96 | 24.92
| 60 |  |  | 6.4 | 6.54 | 6.03 | 5.96 | 24.93
10 | 0 | 150 | 300.285 | 6.4 | 6.54 | 6.03 | 5.96 | 24.93 | 0.9 | 7.1325
| 15 |  |  | 7.12 | 7.25 | 7.01 | 6.9 | 28.28
| 30 |  |  | 7.15 | 7.28 | 7.02 | 6.93 | 28.38
| 30 |  |  | 7.18 | 7.29 | 7.04 | 6.95 | 28.46
| 60 |  |  | 7.2 | 7.29 | 7.06 | 6.98 | 28.53
11 | 0 | 160 | 320.304 | 7.2 | 7.29 | 7.06 | 6.98 | 28.53 | 1.015 | 8.1475
| 15 |  |  | 8.08 | 8.29 | 8.01 | 7.91 | 32.29
| 30 |  |  | 8.12 | 8.32 | 8.05 | 7.94 | 32.43
| 30 |  |  | 8.14 | 8.35 | 8.1 | 7.98 | 32.57
| 60 |  |  | 8.16 | 8.35 | 8.1 | 7.98 | 32.59
12 | 0 | 500 | 1810.28 | 8.16 | 8.35 | 8.1 | 7.98 | 32.59 | 3.32 | 11.4675
15
30
30
| 60 |  |  | 6.48 | 12.97 | 14.55 | 11.87 | 45.87
13 | 0 | 560 | 2027.5136 | 6.48 | 12.97 | 14.55 | 11.87 | 45.87 | 0.445 | 11.9125
15
30
30
| 60 |  |  | 6.8 | 13.25 | 15.1 | 12.5 | 47.65
12 |  | 160 | 320.304 | 8.3 | 8.53 | 8.27 | 8.19 | 33.29 | 0.175 | 8.3225
Tested By |  |  | Client Witness |  |  |  |  | PMC Witness
UNLOADING (06-09-2026)
1 | 0 | 150 | 300.285 | 8.3 | 8.53 | 8.27 | 8.19 | 33.29 | -0.0275 | 8.295
| 15 | [6 empty] | 0
| 30 | [6 empty] | 0
| 30 | [6 empty] | 0
| 15 |  |  | 8.26 | 8.52 | 8.24 | 8.16 | 33.18
2 | 0 | 135 | 270.2565 | 8.26 | 8.52 | 8.24 | 8.16 | 33.18 | -0.0275 | 8.2675
| 15 | [6 empty] | 0
| 30 | [6 empty] | 0
| 45 | [6 empty] | 0
| 15 |  |  | 8.23 | 8.5 | 8.21 | 8.13 | 33.07
3 | 0 | 120 | 240.228 | 8.23 | 8.5 | 8.21 | 8.13 | 33.07 | -0.0225 | 8.245
| 15 | [6 empty] | 0
| 30 | [6 empty] | 0
| 45 | [6 empty] | 0
| 15 |  |  | 8.2 | 8.48 | 8.19 | 8.11 | 32.98
4 | 0 | 105 | 210.1995 | 8.2 | 8.48 | 8.19 | 8.11 | 32.98 | -0.0225 | 8.2225
| 15 | [6 empty] | 0
| 30 | [6 empty] | 0
| 45 | [6 empty] | 0
| 15 |  |  | 8.17 | 8.46 | 8.17 | 8.09 | 32.89
5 | 0 | 90 | 180.171 | 8.17 | 8.46 | 8.17 | 8.09 | 32.89 | -0.0525 | 8.17
| 15 | [6 empty] | 0
| 30 | [6 empty] | 0
| 45 | [6 empty] | 0
| 15 |  |  | 8.12 | 8.4 | 8.12 | 8.04 | 32.68
6 | 0 | 75 | 150.1425 | 8.12 | 8.4 | 8.12 | 8.04 | 32.68 | -0.0625 | 8.1075
15
30
45
| 15 |  |  | 8.06 | 8.31 | 8.05 | 8.01 | 32.43
7 | 0 | 60 | 120.114 | 8.06 | 8.31 | 8.05 | 8.01 | 32.43 | -0.085 | 8.0225
15
30
45
| 15 |  |  | 8.01 | 8.22 | 7.95 | 7.91 | 32.09
8 | 0 | 45 | 90.0855 | 8.01 | 8.22 | 7.95 | 7.91 | 32.09 | -0.1225 | 7.9
15
30
45
| 15 |  |  | 7.92 | 8.1 | 7.8 | 7.78 | 31.6
9 | 0 | 30 | 60.057 | 7.92 | 8.1 | 7.8 | 7.78 | 31.6 | -0.18 | 7.72
15
30
45
| 15 |  |  | 7.7 | 7.92 | 7.61 | 7.65 | 30.88
10 | 0 | 15 | 30.0285 | 7.7 | 7.92 | 7.61 | 7.65 | 30.88 | -0.1025 | 7.6175
15
30
45
| 15 |  |  | 7.6 | 7.81 | 7.52 | 7.54 | 30.47
11 | 0 | 0 | 0 | 7.6 | 7.81 | 7.52 | 7.54 | 30.47 | -0.5775 | 7.04
15
30
45
| 15 |  |  | 7.02 | 7.1 | 7.05 | 6.99 | 28.16
12 |  |  |  | 7.02 | 7.1 | 7.05 | 6.99 | 28.16 | 3.39 | 10.43
|  |  |  | 5.5 | 11.9 | 13.4 | 10.92 | 41.72
13 |  |  |  | 5.5 | 11.9 | 13.4 | 10.92 | 41.72 | -0.5475 | 9.8825
|  |  |  | 5.01 | 11.17 | 13.05 | 10.3 | 39.53
14 |  | 0 | 0 | 5.01 | 11.17 | 13.05 | 10.3 | 39.53 | -5.91 | 3.9725
|  |  |  | 2.85 | 1.38 | 3.32 | 8.34 | 15.89
Tested By |  |  |  |  | Client Witness |  |  | PMC Witness